## Introduction
Service Line Inventory Template
Date last updated: July 27, 2022
What is the purpose of this template? The purpose of this draft template is to help water systems and states comply with the service line inventory requirements of the January 15, 2021 Lead and Copper Rule Revisions (LCRR). This template supplements the draft EPA document, Guidance for Developing and Maintaining a Service Line Inventory (2022) by providing fillable forms and tables that water systems can use to document their methods, organize their inventory, submit the initial inventory and inventory updates to the state, and document how they are making the inventory publicly available. This template also provides a checklist for state review. Note that EPA does NOT require systems use this template for their inventory. Refer to EPA's 2022 Inventory Guidance for minimum LCRR inventory requirements, recommendations, and disclaimers.
How is the template organized?
The worksheets in this template are color coded: Yellow sheets are instructions and background. Dark blue sheets are templates for systems. The dark green sheet is a template for states. See the table below for a description of each worksheet. |  | The cells in this template are also color coded: Gray cells are background or instructions. Light blue cells are fillable cells for systems. Aqua cells are the required fields in the Detailed Inventory worksheet. Light green cells are fillable cells for states.
Template Organization
Worksheet Type | Worksheet Name | Description
Background | Template Instructions_System | Contains detailed instructions for systems.
| Template Instructions_States | Contains detailed instructions for states.
| Classifying SLs | Summarizes requirements for classifying the entire service line when ownership is split (i.e., when the system owns a portion and the customer owns a portion).
Templates for Water Systems | PWS Information | For systems to document basic system information.
| Inventory Methods | For systems to document the methods and resources they used to develop and update their inventory.
| Inventory Summary | For systems to provide a summary of their service line inventory, including information on ownership, inventory format, and the number of service lines for each of the four required materials classifications. Systems can enter the totals into this worksheet or automatically generate totals based on information in the Detailed Inventory worksheet.
| Detailed Inventory | Provides a customizable format water systems can use to track materials for each service line in their distribution system. Each row equals one service line connecting the water main to the customer's plumbing. Separate columns track location information, the system-owned portion, the customer-owned portion, other possible sources of lead, information for assigning a tap sample tiering classification, and information for lead service line replacement (LSLR). Systems can customize the worksheet by adding or deleting columns.
| Public Accessibility Doc. | For systems to provide documentation to states on how they met the public accessibility requirements of the LCRR.
Templates for States | State Checklist | Provides a checklist that states can use to determine and document if water systems met all of the January 15, 2021 LCRR requirements for their Initial Inventory including timely submission, required elements, use of information sources, public accessibility, and public notification of service line materials.

## Dropdowns (hidden)
Drop down lists (Internal, DO NOT MODIFY)
Ownership | Basis of materials classification | Field Verification Methods
Select Ownership Type | Previous Materials Evaluation | Customer self-identification
The entire service line is owned by the water system | Installation record (e.g., tap card) | CCTV investigation at curb stop - internal
The entire service line is owned by the customer | Installation date after lead ban | CCTV investigation at curb stop - external
Ownership is split, meaning that the system owns and portion and the customer owns a portion | Service line diameter is > 2 inches | Water quality sampling
Other | Service line repair or replacement record | Mechanical excavation at one location
| Predictive model | Mechanical excavation at multiple locations
| Water sampling only with no records | Visual inspection at the meter pit
| Field inspection only with no records | Other
Other
State review of customer notification of service line material
Select "Yes", "No", or "N/A"
Yes
No
N/A
Sensitive subpopulations
No
Yes - School
Yes - Day Care
Yes - Multifamily Home
Yes - Other

## Classifying SLs
Classifying the Entire Service Line When Ownership Is Split
Purpose of this worksheet: To summarize EPA's requirements for classifying the entire service line when ownership is split.
Introduction
In many cases, service line ownership is split meaning that the system owns a portion and the customer owns a portion of the service line. Exhibit 1 below is a diagram of a possible division in service line ownership between the water system and customer. While the LCRR requires the inventory to categorize each service line or portions of the service line where ownership is split, a single classification per service line is also needed to support various LCRR requirements, such as lead service line replacement (LSLR), tap sampling, and risk mitigation. Table 1 below indicates how to classify the material for the entire service line when ownership is split between the water system and customer. For more information, see EPA's, Guidance for Developing and Maintaining a Service Line Inventory (2022).
Exhibit 1. Example of Service Line Ownership Distinction between the Water System and Customer
Source: Exhibit 2-2 of Guidance for Developing and Maintaining a Lead Service Line Inventory (USEPA, 2022).
Table 1: Classification of Entire Service Line When Ownership is Split
System-Owned Portion | Customer-Owned Portion | Classification for Entire Service Line
Lead | Lead | Lead
Lead | Galvanized Requiring Replacement | Lead
Lead | Non-lead | Lead
Lead | Lead Status Unknown | Lead
Non-lead | Lead | Lead
Non-lead and never previously lead | Non-lead, specifically galvanized pipe material | Non-lead
Non-lead | Non-lead, material other than galvanized | Non-lead
Non-lead | Lead Status Unknown | Lead Status Unknown
Non-lead, but system is unable to demonstrate it was not previously Lead | Galvanized Requiring Replacement | Galvanized Requiring Replacement
Lead Status Unknown | Lead | Lead
Lead Status Unknown | Galvanized Requiring Replacement | Galvanized Requiring Replacement
Lead Status Unknown | Non-lead | Lead Status Unknown
Lead Status Unknown | Lead Status Unknown | Lead Status Unknown
Source: Exhibit 2-3 of Guidance for Developing and Maintaining a Service Line Inventory (USEPA, 2022).

## PWS Information
PWS Information
Purpose of this worksheet: For water systems to document basic system information.
Facility Information
Water System Name:
Stonington Water Company
PWSID: | Population Served (number of people): | Number of Service Connections: | PWS Type:
ME0091510 | 652.5 | 261 | CWS NTNCWS
If you are a CWS, do multi-family residences comprise at least 20% of the structures you serve? |  |  | No
Mailing Address
Street or P.O. Box:
P.O. Box 9
City or Town: |  | State: | Zip Code:
Stonington |  | Maine | 4681
System Contact Person
Name: |  | Title:
Kathleen Billings |  | Town Manager
Telephone: |  | Email:
(207) 367-2351 |  | townmanager@stoningtonmaine.org
Person Who Prepared Inventory (if different from above)
Name: |  | Title/Affiliation:
Matt Betts |  | Superintendent
Telephone: |  | Email:
(207) 367-2351 |  | stoningtonwaterco@stoningtonmaine.org

## Inventory Methods
Inventory Methodology
PWS Name: Stonington Water Company
PWSID: ME0091510
Enter Date Last Updated: | October 8, 2024
Purpose of this worksheet: For water systems to document the methods and resources they used to develop and update their inventory.
Part 1: Historical Records Review
Type of Record | Describe the Records Reviewed for Your Inventory and Indicate Your Level of Confidence (e.g., Low, Medium, or High)
1. Previous Materials Evaluation Example: Locations of Tier 1 lead tap sampling locations that are served by a lead service line.
2. Construction Records and Plumbing Codes Examples: Local ordinance adopting an international plumbing code. Permits for replacing lead service lines. | Services installed in or after 1989 are being considered Non-Lead (NL) due to the 1986 lead ban and the 1989 DWP cutoff for when these materials can be considered as such.
3. Water System Records Examples: Capital improvement plans. Standard operating procedures. Engineering standards. | Available plans for the water distribution system were reviewed.
4. Distribution System Inspections and Records Examples: Distribution system maps. Tap cards. Service line repair/replacement records. Inspection records. Meter installation records. | Existing service tie cards were used to help determine service line materials.
5. Additional Records Required by Your State
6. Other Records
Part 2: Identifying Service Line Material During Normal Operations
1. During which normal operating activities are you collecting information on service line material? Check all that apply.
Water meter reading | Water main repair or replacement
Water meter repair or replacement | Backflow prevention device inspection
Service line repair or replacement | Other
If "Other", please explain:
In 2024, staff inspected service lines inside the structures for the LSLI, used customer-completed surveys, and institutional knowledge.
2. Did you develop or revise standard operating procedures to collect service line material information during normal operation? |  | Yes
If "Yes", please describe:
The procedure used to inventory the service line materials were from the LSLI instructions and RCAP training class.
Part 3: Service Line Investigations
1. Identify the service line investigation methods your system used to prepare the inventory (check all that apply). If a water system chooses an investigation method not specified by the state under 40 CFR §141.84(a)(3)(iv), state approval is required. Note that investigations are not required by the LCRR but can be used by systems to assess accuracy of historical records and gather information when service line material is unknown.
Visual Inspection at the Meter Pit | Water Quality Sampling - Other
Customer Self-Identification | Mechanical Excavation
CCTV Inspection at Curb Box - External | Vacuum Excavation
CCTV Inspection at Curb Box - Internal | Predictive Modeling
Water Quality Sampling - Targeted | Other
Water Quality Sampling - Flushed
Water Quality sampling - Sequential
If "Other", please explain:
Used staff institutional knowledge from previous service line leak excavations.
2. If "Predictive Modeling", please briefly describe the model and inputs used:
3. How did you prioritize locations for service line materials investigations? For example, did you consider environmental justice and/or sensitive populations, did you use predictive modeling, and/or did you target areas with high number of unknowns?
Visited properties that were available for an immediate onsite visit. Scheduled site visits for those not home during the initial door-to-door contact by using doorknob hangers. Customers contacted the Water Company staff to schedule when the onsite inspection could occur.

## Inventory Summary
Inventory Summary
PWSID: ME0091510
Enter Date Last Updated: | October 8, 2024
Purpose of this worksheet: For water systems to provide a summary of their service line inventory, including information on ownership, inventory format, and the number of service lines for each of the four required materials classifications.
Part 1. General Information
1. Is this the Initial Inventory or an Inventory Update? |  | Initial Inventory
2a. Who owns the service lines in your system? If other, please explain below. |  | Ownership is split, meaning that the system owns and portion and the customer owns a portion
2b. Is there documentation that defines service line ownership in your system, such as a local ordinance? If yes, please describe below and explain where ownership is split (e.g., property line, curb stop). |  | Yes
Water Company Terms and Conditions state customer ownership starts at the curb stop.
3a. Describe when lead service lines were generally installed in your system.
It is unknown if lead service lines were ever installed prior to the Maine ban on such in 1926.
3b. When were lead service lines banned in your system? Reference the state or local ordinance that banned the use of lead in your system.
The 1926 Maine ban on lead lines.
4. Do you have lead goosenecks, pigtails or connectors in your system? |  | Don't Know
5. What is your overall level of confidence in the inventory (i.e., "Low", "Medium", or "High.") Please explain your rationale below.
High. Comprehensive service tie and repair records, as-built plans, and dates of service line replacement. Visual inspection of customer portion of the services.
Part 2. Inventory Format
Describe your inventory format in the space provided below (e.g., the Detailed Inventory worksheet, custom spreadsheet, GIS map). Provide the filename and/or web address if applicable. Note that the state may require you to submit your detailed inventory of each service line in your distribution system.
Detailed Inventory worksheet using the EPA provided Excel long format spreadsheet.
Part 3. Inventory Summary Table 1
If you are using the Detailed Inventory worksheet, the classifications you select in the Column "Entire Service Line Material Classification" (Column X) will be used to calculate the total number of service lines for each of the four material classifications below. Otherwise, enter the number of service lines in the aqua-colored cells. Remember this is the classification for the entire service line.
Service Line Material Classification | Definition |  | Total Number of Service Lines (REQUIRED to be reported under the LCRR)
Lead | Any portion of the service line is known to be made of lead.2 |  | 0
Galvanized Requiring Replacement (GRR) | The service line is not made of lead, but a portion is galvanized and the system is unable to demonstrate that the galvanized line was never downstream of a lead service line. |  | 4
Non-Lead | All portions of the service line are known NOT to be lead or GRR through an evidence-based record, method, or technique. |  | 257
Lead Status Unknown | The service line material is not known to be lead or GRR. For the entire service line or a portion of it (in cases of split ownership), there is not enough evidence to support material classification. |  | 0
TOTAL |  |  | 261
Notes
1 This summary table is for reporting material for the entire service line connecting the water main to the customer's plumbing. See the Classifying SLs worksheet for additional guidance on assigning a materials classification to the entire service line when ownership is split. Remember that systems must track the system-owned and customer-owned portions separately in their inventory.
2 A lead-lined galvanized service line is consistent with the definition of an LSL under the LCRR (“a portion of pipe that is made of lead, which connects the water main to the building inlet”) (40 CFR §141.2) and must therefore be classified in the inventory as an LSL. Do NOT, however, count non-lead service lines with a lead gooseneck or pigtail as lead service lines unless required by your state.

## Detailed Inventory
Detailed Inventory
Stonington Water Company
PWSID:ME0091510
Date Last Updated: October 8, 2024
Purpose of this worksheet: To provide a customizable format water systems can use to track materials for each service line in their distribution system. General Instructions: Each row in this worksheet represents one service line connecting the water main to the customer's plumbing. The worksheet includes required and recommended elements; the columns with the aqua shading are required by the LCRR. Systems can customize by adding or deleting columns. Important notes for each column are in Row 12; also see the Template Instructions worksheet for detailed instructions. Note that users can freeze panes to enable them to see the headings and notes when entering data. The worksheet includes examples in rows 13 - 20 and is formatted for approximately 10,000 entries.
Location Information |  |  |  |  | System-Owned Portion | [8 empty] | Customer-Owned Portion | [7 empty] | Entire Service Line Material Classification | Other Potential Sources of Lead |  |  | Additional Information to Assign Tap Monitoring Tiering |  |  |  | Lead Service Line Replacement (LSLR)
Unique Service Line ID | Location Identifier |  | Sensitive Population? (Yes/No) | Disadvantaged Neighborhood? (Yes/No) | System-Owned Portion Service Line Material Classification | If Non-Lead in Column G, Was Material Ever Previously Lead? | Service Line Installation Date | Service Line Size | Basis of Material Classification | Was the Service Line Material Field Verified? | If "Yes" Service Line Material Was Field Verified: |  | Notes | Customer-Owned Portion Service Line Material Classification | Service Line Installation Date | Service Line Size | Basis of Material Classification | Was the Service Line Material Field Verified? | If "Yes" Service Line Material Was Field Verified: |  | Notes |  | Is there a Lead Connector? | Is there Lead Solder in the Service Line? | Describe Other Fittings and Equipment Connected to the Service Line that Contain Lead | Building Type Connected to Service Line | Point-of-Entry or Point-of-Use Treatment Present? | Does the Interior Building Plumbing Contain Copper Pipes with Lead Solder Installed Before Your State's Lead Ban (Generally 1986 - 1988)? | Current LCR Sampling Site? | Date of System-owned LSLR | Date of Customer-owned LSLR
| Street Address | Other Location Identifier | [8 empty] | Describe the Field Verification Method | Enter the Date of Field Verification | [6 empty] | Describe the Field Verification Method | Enter the Date of Field Verification
A Unique ID is recommended for each service line. | Water systems must track addresses of all service lines in their internal inventory. For the publicly accessible version, location identifiers are required for lead and galvanized requiring replacement. If the system does not use addresses for their location identifier, other options could include GPS coordinates, landmark, intersection, block, or other details to specify service line locations. |  | Select Yes if sensitive subpopulation, e.g., day care, school, multifamily home. If Yes-Other, describe in the Notes field. | Does location meet state affordability guidelines or other measures? | Dropdown list includes recommended subclassifications. If "Non-Lead Other", describe in Notes field | Select Yes, No, or Don't know. Important for determining if downstream/ customer-owned galvanized service line requires replacement | Date, year, or estimated date range when the service line was installed or replaced | Diameter in inches | Select option from drop down list. If "Other," describe in the Notes field | Select Yes or No | Select option from drop down list. If "Other," describe in the Notes field | Enter approximate date of field verification or date that the record was updated | Can use this field for documenting additional relevant information, including when classification changes. | Dropdown list includes recommended subclassifications. If non-lead other, describe in Notes field. | Date, year, or estimated date range when the service line was installed or replaced | Diameter in inches | Select option from drop down list. If "Other," describe in the Notes field | Select Yes or No | Select option from drop down list. If "Other," describe in the Notes field | Enter approximate date of field verification or date that record was updated | Can use this field for documenting additional relevant information, including when classification changes. | Dropdown list includes four required service line classifications of Lead, Non-lead, Galvanized Requiring Replacement, or Unknown | For example, lead gooseneck or pigtail where the water main is connected to the service line | Select Yes, No, or Don't Know | For example, backflow preventer or meter containing lead | Note: This information may be helpful for identifying lead tap monitoring locations.
4A,49 | 72 Moose Island, Sto |  | No | No | Non-Lead - Plastic | No | 2007-05-07 | 2 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-04-05 |  | Non-Lead - Plastic | 2007 | 2 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-04-05 |  | Non-Lead | No | No |  | Other | Unknown | Unknown | No
4B,33 | 1 Thoroufare Rd |  | No | No | Non-Lead - Copper | No | 2002-10-03 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2002 | 1 | Installation date after lead ban | Yes | Customer self-identification | 2024-05-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
4B,37 | 62 Greanhead Rd. |  | No | No | Non-Lead - Plastic | No | 2009-08-01 | 1 | Installation date after lead ban | Yes |  |  |  | Non-Lead - Plastic | 2009 | 1 | Installation date after lead ban | Yes | Customer self-identification | 2024-05-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
4B,47A | 25 Ocean Street |  | No | No | Non-Lead - Plastic | No | 2009-07-28 | 3/4 | Installation date after lead ban | Yes |  |  |  | Non-Lead - Plastic | 2010 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
4B,47A | 38 Ocean Street |  | No | No | Non-Lead - Plastic | No | 1992-11-04 | 2 | Installation date after lead ban | Yes |  |  |  | Non-Lead - Plastic | 1992 | 2 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-23 |  | Non-Lead | No | No |  | Other | No | Unknown | No
5,27 | 15 Larrabee Road | Building A | No | No | Non-Lead - Plastic | No | 2007-06-19 | 1 | Installation date after lead ban | Yes |  |  |  | Non-Lead - Plastic | 2007 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,29 | 15 Larrabee Road | Building B | No | No | Non-Lead - Plastic | No | 2007-06-19 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2007 | 1 | Installation date after lead ban | Yes | Customer self-identification | 2024-05-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,28 | 11 Larrabee Road |  | No | No | Non-Lead - Plastic | No | 2017-08-20 | 1 | Installation date after lead ban | Yes |  |  |  | Non-Lead - Plastic | 2017 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,32 | 8 Cemetary Road |  | No | No | Non-Lead - Copper | No | 2024-08-29 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-29 |  | Non-Lead - Plastic | 1974 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,33A | 5 Sunset Ave. |  | No | No | Non-Lead - Copper | No | 2024-08-26 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-26 |  | Non-Lead - Plastic | 1987-11-18 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-04-25 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,33 | 15 Sunset Ave. |  | No | No | Non-Lead - Copper | No | 2024-08-27 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-27 |  | Non-Lead - Plastic | 1986-05-22 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-04-25 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,35 | 14 Larrabee Rd. |  | No | No | Non-Lead - Plastic | No | 2004-10-07 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1988-07-12 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-04-27 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,39 | 37 Sunset Ave. |  | No | No | Non-Lead - Copper | No | 2024-08-27 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-27 |  | Non-Lead - Plastic | 1996-06-13 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,42 | 43 Sunset Ave. |  | No | No | Non-Lead - Copper | No | 2024-08-27 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-28 |  | Non-Lead - Plastic | 1990 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,51A | 20 Old Quarry Road |  | No | No | Non-Lead - Plastic | No | 2008-09-13 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2008-09-13 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2023-08-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,53 | 36 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2003-07-09 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
5,54 | 38 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Galvanized | 1981-03-05 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-13 |  | Galvanized Requiring Replacement | No | No |  | Single Family Residence | No | Unknown | No
5,54A | 44 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1996-05-08 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5.57 | 58 School Street |  | No | No | Non-Lead - Copper | No | 1998-05-01 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1998-05-01 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-04-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,58 | 35 School Street |  | No | No | Non-Lead - Copper | No | 2012-12-05 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2012-12-05 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,59 | 37 School Street |  | No | No | Non-Lead - Copper | No | 1990-11-07 | 3/4 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2024-06-01 |  | Non-Lead - Plastic | 1990-11-07 | 3/4 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2024-06-01 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,60 | 43 School Street |  | Yes - Other | No | Non-Lead - Copper | No | 1988-09-12 | 2 | Installation record (e.g., tap card) | No |  |  | Office Building | Non-Lead - Plastic | 2003-04-09 | 2 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-08 |  | Non-Lead | No | No |  | Building | No | Unknown | No
5,61 | 10 Memorial Lane |  | No | No | Non-Lead - Copper | No | 2003-06-11 | 2 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2012-12-04 | 2 | Installation date after lead ban | No | Visual inspection at the meter pit | 2024-08-08 |  | Non-Lead | No | No |  | Building | No | Unknown | No
5,62 | 49 School Street |  | No | No | Non-Lead - Copper | No | 1993-12-01 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1993-12-01 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-08 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,63 | 53 School Street |  | No | No | Non-Lead - Copper | No | 1998-01-22 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1998-04-22 | 3/4 | Installation date after lead ban | No | Visual inspection at the meter pit | 2024-08-08 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,64 | 7 Cemetary Road |  | No | No | Non-Lead - Copper | No | 2024-08-28 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-28 |  | Non-Lead - Plastic | 1974-10-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-08 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,69B | 59 School Street |  | No | No | Non-Lead - Copper | No | 2024-08-28 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-08-28 |  | Non-Lead - Plastic | 1988-07-21 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-08 |  | Non-Lead | No | No |  | Building | No | Unknown | No
5,73 | 7 North Seabreeze |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2016 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
5,75 | 16 North Main |  | No | No | Non-Lead - Copper | No | 2016 | 1 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1986-08-05 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,02 | 25 North Main |  | No | No | Non-Lead - Copper | No | 2016 | 1 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-07-09 | New customer 7/9/2024 | Non-Lead - Plastic | 2024-07-09 | 1 | Installation date after lead ban | Yes | Mechanical excavation at multiple locations | 2024-07-09 | New customer 7/9/2024 | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,22 | 40 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1976-03-05 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1976-03-05 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,23 | 24 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1975-11-09 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2012-06-01 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,24 | 28 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1975-01-09 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2003 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,26 | 44 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1976-10-15 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1976-10-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,27 | 48 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1978-09-03 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1978-09-03 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,28 | 43 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1975-01-24 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1975-01-24 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,29 | 51 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1975-11-30 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1975-11-30 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
6,30 | 49 Indian Point Road |  | No | No | Non-Lead - Copper | No | 1975-11-30 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1975-11-30 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,02 | 19 Greenhead Road |  | Yes - Multifamily Home | No | Non-Lead - Plastic | No | 1994-04-28 | 1 | Installation date after lead ban | No |  |  | 2 unit apartment | Non-Lead - Plastic | 1994-04-28 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
7A,02A | 25 Greenhead Road |  | No | No | Non-Lead - Plastic | No | 2024-04-28 | 1 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-07-12 |  | Non-Lead - Plastic | 2023-07-12 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2023-07-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,03 | 15 Greenhead Road |  | No | No | Non-Lead - Plastic | No | 1994-04-28 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2024-04-28 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,07 | 3 Old Quarry Road |  | No | No | Non-Lead - Copper | No | 1985-08-27 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1985-08-27 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,08 | 131 West Main |  | No | No | Non-Lead - Copper | No | 1997-07-11 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1997-07-11 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-07-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,09 | 5 Old Quarry Road |  | No | No | Non-Lead - Plastic | No | 2002-04-16 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 2002-04-16 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,10 | 11 Old Quarry Road |  | No | No | Non-Lead - Plastic | No | 1994-07-24 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1994-07-22 | 1 | Installation date after lead ban | Yes | Customer self-identification | 2024-07-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
7A,11 | 15 Old Quarry Road |  | No | No | Non-Lead - Plastic | No | 2008-09-13 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2008-09-13 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2023-06-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,14 | 119 West Main |  | No | No | Non-Lead - Copper | No | 1983-03-05 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2015-08-12 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,15 | 111 West Main |  | No | No | Non-Lead - Copper | No | 2010-11-09 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2010-11-09 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,16 | 112 West Main |  | No | No | Non-Lead - Copper | No | 1976-02-15 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1976-02-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,20 | 6 Honk Way |  | No | No | Non-Lead - Copper | No | 1993-07-27 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1993-07-27 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,21 | 8 Ocean Street |  | No | No | Non-Lead - Copper | No | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,22 | 7 Ocean Street |  | No | No | Non-Lead - Copper | No | 9/12/!977 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,23 | 22 Allen Street |  | No | No | Non-Lead - Plastic | No | 2008-05-09 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2008-05-09 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-07-25 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,30 | 21 Ocean Street |  | No | No | Non-Lead - Plastic | No | 1977-09-12 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,24 | 24 Allen Street |  | No | No | Non-Lead - Copper | No | 1992-04-13 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-04-13 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-07-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,28 | 20 Ocean Street |  | No | No | Non-Lead - Plastic | No | 1992-11-16 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992-11-16 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,32 | 8 Richardson Lane |  | No | No | Non-Lead - Plastic | No | 2004-06-10 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2004-06-10 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-04-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,35 | 20 Greenhead Lane |  | No | No | Non-Lead - Plastic | No | 2002-10-04 | 1 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2022-06-05 |  | Non-Lead - Plastic | 2002-10-04 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,36 | 23 Allen Street |  | No | No | Non-Lead - Copper | No | 1977-09-12 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1984-06-20 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2023-05-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,37 | 3 Farrel Street |  | No | No | Non-Lead - Copper | No | 1977-09-12 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2023-06-08 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,38 | 13 Allen Street |  | No | No | Non-Lead - Copper | No | 1994-02-09 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1994-02-09 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,39 | 11 Allen Street |  | No | No | Non-Lead - Copper | No | 1992 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,40 | 7 Allen Street |  | No | No | Non-Lead - Copper | No | 1982-09-15 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1982-09-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,41 | 6 Greadhead Road |  | No | No | Non-Lead - Copper | No | 2017-08-10 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-25 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,44 | 5 Mels Way |  | No | No | Non-Lead - Plastic | No | 1991-08-16 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1991-08-16 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,46 | 9 Farrel Street |  | No | No | Non-Lead - Plastic | No | 1992 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,52 | 3 Greenhead Lane |  | No | No | Non-Lead - Plastic | No | 1994-04-28 | 3/4 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-06-23 |  | Non-Lead - Plastic | 1994-04-28 | 1 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-06-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7A,53 | 22 Greenhead Road |  | No | No | Non-Lead - Plastic | No | 1994-04-30 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1994-04-30 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2023-10-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,03 | 3 Waterveiw Lane |  | No | No | Non-Lead - Copper | No | 2009 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2009 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-07-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,04 | 6 Arvards L:ane |  | No | No | Non-Lead - Copper | No | 2009 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2009 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,05 | 4 Waterveiw Lane |  | No | No | Non-Lead - Copper | No | 2009 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2009 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,06 | 91 West Main |  | No | No | Non-Lead - Copper | No | 1976 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1976 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,07 | 5 Arvard Lane |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1983 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B/09 | 5 McDonald Lane |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1994 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,11 | 16 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1988-08-23 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,13 | 14 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1988-08-27 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,14 | 12 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1988-08-27 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,15 | 4 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Galvanized | 1977-03-18 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-22 |  | Galvanized Requiring Replacement | No | No |  | Single Family Residence | No | Unknown | No
7B,16 | 18 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2015 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-07-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,17 | 20 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1991-05-30 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-24 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,18 | 22 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1989-06-18 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2023-07-24 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,19 | 24 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1984-04-20 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,20 | 26 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1993-05-10 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,22 | 32 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1990-03-21 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,23 | 34 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1987-04-10 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,24 | 29 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1980-10-06 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,25 | 7 Church Street |  | No | No | Non-Lead - Copper | No | 1992-07-27 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-07-27 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,26 | 6 Hardie Lane |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1987-09-15 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,27 | 45 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Galvanized | 1987-08-25 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-18 |  | Galvanized Requiring Replacement | No | No |  | Single Family Residence | No | Unknown | No
7B,29 | 26 School Street |  | No | No | Galvanized | No | 1976-09-10 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1976-09-10 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,31 | 20 School Street |  | No | No | Non-Lead - Copper | No | 1994-04-18 | 3/4 | Installation date after lead ban | No |  |  |  | Galvanized | 1994-04-18 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,32 | 1 Church Street |  | No | No | Non-Lead - Copper | No | 1992-07-30 | 3/4 | Installation date after lead ban | No |  |  |  | Galvanized | 1992-07-30 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-29 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,33 | 3 Church Street |  | No | No | Non-Lead - Copper | No | 1992-07-28 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992-07-28 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,34 | 27 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2001-06-13 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,35 | 19 Church Street |  | No | No | Non-Lead - Copper | No | 1992 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-27 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,36 | 17 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1992 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2023-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,37 | 16 Church Street |  | No | No | Non-Lead - Plastic | No | 1992-07-24 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992-07-24 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,38 | 14 Church Strret |  | No | No | Non-Lead - Plastic | No | 2022-08-16 | 1 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2022-08-16 |  | Non-Lead - Plastic | 2022-08-16 | 3/4 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2022-08-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,39 | 10 Church Street |  | No | No | Non-Lead - Copper | No | 1980-07-29 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1980-07-29 | 3/4 | Installation record (e.g., tap card) | Yes | Customer self-identification | 2024-08-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,40 | 7 Opera House Lane |  | No | No | Non-Lead - Plastic | No | 2015 | 1.25 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2015 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2023-09-27 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,41 | 6 Church Street |  | No | No | Non-Lead - Copper | No | 1992-07-27 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-08-27 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-08-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
7B,42 | 4 Church Street |  | No | No | Non-Lead - Copper | No | 1992-08-31 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-08-31 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,43 | 8 School Street |  | No | No | Non-Lead - Copper | No | 1992-07-10 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1989-09-13 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,44 | 5 Opera House Lane |  | No | No | Non-Lead - Plastic | No | 2015 | 1.25 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2015 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-24 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,45 | 1 Opera House Lane |  | Yes - Other | No | Non-Lead - Other | No | 2015 | 6 | Installation date after lead ban | No |  |  | Movie Theater | Non-Lead - Other | 2015 | 6 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-16 |  | Non-Lead | No | No |  | Other | No | Unknown | No
7B,49 | 11 West Main |  | No | No | Non-Lead - Copper | No | 1972-06-12 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1986-09-16 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,50 | 8 Opera House Lane |  | No | No | Non-Lead - Plastic | No | 2015 | 1.25 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2015 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-08 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,51 | 19 West Main |  | No | No | Non-Lead - Copper | No | 1972-03-20 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2023-05-18 | 3/4 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-05-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,51A | 4 Johnny's Way |  | No | No | Non-Lead - Copper | No | 1975-04-16 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1975-04-16 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-21 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,52 | 6 Johnny's Way |  | No | No | Non-Lead - Copper | No | 1992 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,53 | 27 West main |  | No | No | Non-Lead - Copper | No | 1984-05-01 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1984-05-01 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,54 | 39 West Main |  | No | No | Non-Lead - Copper | No | 1981-08-16 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1981-08-16 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,55 | 15 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1987-03-10 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 1987-03-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,56 | 13 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1978-05-23 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,57 | 11 Highland Ave. |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1979-04-21 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,58 | 73 West Main |  | No | No | Non-Lead - Copper | No | 1979-06-03 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1979-06-03 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-09 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,59 | 7 Highland Ave. |  | No | No | Non-Lead - Copper | No | 1995-03-30 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1995-03-30 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-09 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,60 | 79 West Main |  | No | No | Non-Lead - Copper | No | 2015 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2006-04-27 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-08-09 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,61 | 96 West main |  | No | No | Non-Lead - Copper | No | 1987-09-24 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1987-09-24 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,62 | 90 West Main |  | No | No | Non-Lead - Copper | No | 1974-04-22 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1974-09-22 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,63 | 78 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,64 | 76 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,65 | 74 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
7B,67 | 66 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2003-06-16 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-08-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
7B,68 | 60 West Main |  | No | No | Non-Lead - Copper | No | 1973-08-12 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1973-08-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,69 | 58 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-13 |  | Non-Lead | No | No |  | Building | No | Unknown | No
7B,70 | 54 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,72 | 48 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,74 | 3 Andy's Road |  | No | No | Non-Lead - Copper | No | 1975-04-01 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2016 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,75 | 7 Andy's Road |  | No | No | Non-Lead - Copper | No | 1975-04-01 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2014 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,76 | 28 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1990-08-23 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2023-07-16 |  | Non-Lead | No | No |  | Building | No | Unknown | No
7B,76 | 1 Rhode Island |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1990-08-23 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2023-07-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,77 | 8 Andy's Road |  | No | No | Non-Lead - Copper | No | 2003-06-24 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2003-06-24 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-08-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,78 | 8 Rhode Island |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2018-07-26 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-08-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,79 | 4 Rhode Island |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,81 | 18 West Main |  | No | No | Non-Lead - Copper | No | 2011-08-14 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2011-08-14 | 3/4 | Installation date after lead ban | Yes | Customer self-identification | 2024-09-17 |  | Non-Lead | No | No |  | Building | No | Unknown | No
7B,82 | 10 West Main |  | No | No | Non-Lead - Copper | No | 1971 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1971 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,83 | 8 Fish Pier Lane |  | No | No | Non-Lead - Copper | No | 1984-08-13 | 2 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1984-09-13 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-09-20 |  | Non-Lead | No | No |  | Building | No | Unknown | No
7B,84 | 8 West Main |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2009 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-09-20 |  | Non-Lead | No | No |  | Building | No | Unknown | No
7B,85 | 3 Main Street |  | No | No | Non-Lead - Copper | No | 1976-05-13 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1976-05-13 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
7B,86 | 8 Gray Lane |  | No | No | Non-Lead - Copper | No | 1984-09-28 | 1.5 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1984-09-28 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | Yes | Unknown | No
7B,87 | 7 Gray Lane |  | No | No | Non-Lead - Copper | No | 1984-09-28 | 1.5 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1984-09-28 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,01 | 17 Main Street |  | No | No | Non-Lead - Copper | No | 1992-10-29 | 1.5 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-10-29 | 1.5 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-09-25 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,02 | 5 School Street |  | No | No | Non-Lead - Copper | No | 1972 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1994 | 1 | Installation date after lead ban | Yes | Customer self-identification | 2024-07-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,2A | 6 Main Street |  | No | No | Non-Lead - Copper | No | 1976 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1976 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,03 | 9 School Street |  | No | No | Non-Lead - Copper | No | 1972 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1994 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,04 | 13 School Street |  | No | No | Non-Lead - Copper | No | 1979-08-28 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1979-08-28 | 3/4 | Installation record (e.g., tap card) | Yes | Customer self-identification | 2024-07-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,05 | 17 School Street |  | No | No | Non-Lead - Copper | No | 1977-07-06 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1996-08-05 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,05 | 21 School Street |  | No | No | Non-Lead - Copper | No | 1999-08-09 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1999-08-09 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,05 | 19 School Street |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 1999-08-10 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1999-08-10 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
8A,06 | 23 School Street |  | No | No | Non-Lead - Copper | No | 1974-08-15 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1974-08-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,07 | 29 School Street |  | No | No | Non-Lead - Copper | No | 1976-05-10 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1976-05-10 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,08 | 33 School Street |  | No | No | Non-Lead - Copper | No | 1979-09-10 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2024-06-08 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-06-08 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,09 | 31 School Street |  | No | No | Non-Lead - Copper | No | 2001-05-08 | 3/4 | Installation date after lead ban | No |  |  |  | Galvanized | 2001-05-08 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,11A | 16 Pink Street |  | No | No | Non-Lead - Plastic | No | 1986-05-16 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2009-08-24 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-05 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,15 | 18 Main Street |  | No | No | Non-Lead - Copper | No | 1984-05-15 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1984-05-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,16 | 24 Main Street |  | No | No | Non-Lead - Copper | No | 1984-05-09 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1994-05-09 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-03 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,16A | 26 Main Street |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 1992-10-14 | 3/4 | Installation date after lead ban | No |  |  | 2 unit apartment Building | Non-Lead - Copper | 1992-10-14 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-10 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
8A,17 | 32 Main Street |  | Yes - Other | No | Non-Lead - Copper | No | 2005-07-25 | 2 | Installation record (e.g., tap card) | No |  |  | Town Office | Non-Lead - Copper | 2005-07-25 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-10-03 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,19 | 40 Main Street |  | No | No | Non-Lead - Copper | No | 1973-05-23 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1973-05-23 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,20 | 21 Main Street |  | No | No | Non-Lead - Copper | No | 1982-07-06 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2021-03-01 |  | Non-Lead - Plastic | 2021-03-01 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2021-03-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,21 | 23 Main Street |  | No | No | Non-Lead - Copper | No | 1992-08-07 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1992-08-07 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,22 | 27 Main Street |  | No | No | Non-Lead - Copper | No | 1977-08-30 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2023-05-01 |  | Non-Lead - Copper | 1977-08-30 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2023-05-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,22 | 27 Main Street |  | No | No | Non-Lead - Copper | No | 2003-11-12 | 1.5 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-05-01 |  | Non-Lead - Copper | 2003-11-12 | 1.5 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-05-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,23 | 31 Main Street |  | No | No | Non-Lead - Copper | No | 1981-08-06 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1981-08-06 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,25 | 45 Main Street |  | No | No | Non-Lead - Copper | No | 1979-07-09 | 2 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1979-07-09 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-09-30 |  | Non-Lead | No | No |  | Other | No | Unknown | No
8A,26 & 26A | 51 Main Street |  | No | No | Non-Lead - Copper | No | 1978-06-06 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2022-11-15 |  | Non-Lead - Plastic | 1978-06-06 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2022-11-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,28 | 59 Main Street |  | No | No | Non-Lead - Copper | Yes | 1978-10-25 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1978-10-25 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,29 | 56 Main Street |  | No | No | Non-Lead - Copper | No | 1996-09-16 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1996-09-16 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,30 | 50 Main Street |  | No | No | Non-Lead - Copper | No | 1977-03-22 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2022-11-15 |  | Non-Lead - Plastic | 1977-03-22 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,30A | 52 Main Street |  | No | No | Non-Lead - Copper | No | 2015-11-01 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 2015-11-01 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-09-16 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,31 | 44 Main Street |  | No | No | Non-Lead - Copper | No | 1979-10-04 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1979-10-04 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-16 |  | Non-Lead | No | No |  | Other | No | Unknown | Yes
8A,32A | 9 Pink Street |  | No | No | Non-Lead - Copper | No | 2001-06-11 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2001-06-11 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,32C | 54 Main Street |  | No | No | Non-Lead - Copper | No | 2015-11-01 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 2015-11-01 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-04 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,33 | 12 Cottage Lane |  | No | No | Non-Lead - Plastic | No | 1996-04-05 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 2018-09-06 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-09-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,39 | 11 Robbins Street |  | No | No | Non-Lead - Copper | No | 1992-08-12 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-08-12 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-09-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
8A,43 | 16 North Seabreeze |  | No | No | Non-Lead - Copper | No | 2016-12-01 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2016-12-01 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-09-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
8A,44 | 8 North Seabreeze |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2006-08-31 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-23 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,45 | 4 North Seabreeze |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1973-11-01 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-23 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
8A,46 | 7 Robbins Street |  | No | No | Non-Lead - Copper | No | 2023-07-15 | 2 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2023-07-15 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2023-07-15 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,47 | 6 Robbins Street |  | No | No | Non-Lead - Copper | No | 1992-07-16 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-07-16 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-19 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A48 | 60 Main Street |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 1996-09-16 | 3/4 | Installation date after lead ban | No |  |  | 5 Unit Condo | Non-Lead - Plastic | 1996-09-16 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
8A,50 | 66 Main Street |  | No | No | Non-Lead - Copper | No | 1994-07-05 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1994-07-05 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,51 | 68 Main Street |  | Yes - Other | No | Non-Lead - Copper | No | 1982-05-26 | 3/4 | Installation record (e.g., tap card) | No |  |  | Resturant with 2 condos upstairs | Non-Lead - Copper | 1982-05-26 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,52 | 68 Main Street |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 1978-10-09 | 2 | Installation record (e.g., tap card) | No |  |  | 2 Unit Condo | Non-Lead - Copper | 1978-10-09 | 2 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-30 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
8A53 | 70 Main Street |  | No | No | Non-Lead - Copper | No | 1993-08-05 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2013-05-06 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,54 | 86 Main Street |  | No | No | Non-Lead - Copper | No | 2016-06-05 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1987-03-10 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-07 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,55 | 80 Main Street |  | No | No | Non-Lead - Copper | No | 2016-06-05 | 3/4 | Service line repair or replacement record | No |  |  |  | Galvanized | 1992-06-04 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-09 |  | Galvanized Requiring Replacement | No | No |  | Single Family Residence | No | Unknown | No
8A,58 | 69 Main Street |  | No | No | Non-Lead - Copper | No | 1984-05-07 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1984-05-07 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-06 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,59 | 5 Atlantic Ave |  | No | No | Non-Lead - Copper | No | 1981 | 2 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1981 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-08-06 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,63 | 9 Atlantic Ave |  | No | No | Non-Lead - Copper | No | 1992 | 2 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1972 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,63 | 9 Atlantic Ave |  | No | No | Non-Lead - Plastic | No | 1981 | 2 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1981 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,64 | 13 Atlantic Ave |  | No | No | Non-Lead - Plastic | No | 2007-08-15 | 2 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2007-08-15 | 2 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-10-01 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,65 | 28 Atlantic Ave |  | No | No | Non-Lead - Plastic | No | 1999 | 2 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2022-09-23 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2022-09-23 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A70 | 2 Atlantic Ave |  | No | No | Non-Lead - Plastic | No | 1997 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1997 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-07 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A,71 | 3 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1974 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2022-06-11 |  | Non-Lead - Other | 1974 | 1.25 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-13 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,72 | 7 Seabreeze Ave |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 1972-08-15 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2022-12-21 | 3 Unit Apartment | Non-Lead - Plastic | 1972-08-05 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No
8A,73 | 9 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1992-06-08 | 3/4 | Installation date after lead ban | No |  |  |  | Galvanized | 1992-06-08 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,74 | 13 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 2000-08-02 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 2000-08-02 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,28 | 16 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1982 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2023-07-02 |  | Non-Lead - Copper | 1982 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,75 | 15 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1974-09-16 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1974-09-16 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,75A | 17 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1977-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,76 | 19 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1975-07-10 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1994-09-08 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,77 | 21 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1976-08-05 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Galvanized | 1976-08-05 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,78 | 25 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 2009-09-18 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 2009-09-18 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-18 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8A/80 | 27 Seabreeze Ave |  | No | No | Non-Lead - Other | No | 1982-04-20 | 4 | Service line diameter is > 2 inches | No |  |  |  | Non-Lead - Other | 1982-04-20 | 4 | Service line diameter is > 2 inches | Yes | Visual inspection at the meter pit | 2024-09-18 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8B,04 | 13 N. Seabreeze |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1987-03-05 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,05 | 9 N Seabreeze |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1975-07-10 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,06 | 7 North Seabreeze |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1992 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,07 | 3 N Seabreeze |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2014 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-09-05 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,09 | 6 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1989-03-06 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-05 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,10 | 24 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2014-06-24 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-09-05 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,12 | 34 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1986 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,13 | 38 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 9/31/2006 | 1 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-09-05 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,14 | 6 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2017 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-11 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,15 | 10 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1974-12-31 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,16 | 8 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 1974-12-31 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,17 | 21 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2018-09-05 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-12 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,18 | 19 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2018-08-07 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,21 | 7 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1975-01-02 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,22 | 3 N. Main Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1975-03-08 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-14 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,23 | 9 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1976-05-03 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,24 | 8 Seabreeze Ave. |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2004-11-29 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-24 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B25 | 10 Seabreeze Ave. |  | No | No | Non-Lead - Copper | No | 1972-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2022-12-22 |  | Non-Lead - Plastic | 1972-09-12 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-18 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8B,26 | 12 Seabreeze Ave. |  | No | No | Non-Lead - Copper | No | 1974-12-24 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1974-12-24 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
8B,27 | 11 Pleasant Street |  | No | No | Non-Lead - Copper | No | 2005-07-08 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2004-11-29 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-10 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,28 | 16 Seabreeze Ave |  | No | No | Non-Lead - Copper | No | 1981-03-02 | 3/4 | Installation record (e.g., tap card) | Yes | Mechanical excavation at one location | 2023-03-17 |  | Non-Lead - Plastic | 1981-03-02 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2023-03-17 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,30 | 20 Seabreeze Ave. |  | No | No | Non-Lead - Copper | No | 1975-07-09 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1975-07-09 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-06 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,31 | 22 Seabreeze Ave. |  | No | No | Non-Lead - Copper | No | 1992-06-08 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Copper | 1992-06-08 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,32 | 24 Seabreeze Ave. |  | No | No | Non-Lead - Plastic | No | 2024-06-18 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-06-18 |  | Non-Lead - Plastic | 2001-06-01 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-01 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,33 | 8 Bayveiw Street |  | No | No | Non-Lead - Plastic | No | 2024-06-18 | 3/4 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2024-06-18 |  | Non-Lead - Plastic | 2001-06-01 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-06-01 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,34 | 17 Pleasant Street |  | No | No | Non-Lead - Plastic | No | 1984-10-18 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1984-10-18 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,34A | 12 Bayveiw Street |  | No | No | Non-Lead - Copper | No | 1976-05-14 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1976-05-14 | 1 | Service line repair or replacement record | Yes | Mechanical excavation at one location | 2023-02-21 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,37 | 16 Pleasant Street |  | No | No | Non-Lead - Plastic | No | 1984-10-18 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1984-10-18 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-18 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,40 | 9 Granite Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2007-08-22 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-07-21 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,41 | 14 Pleasant Street |  | No | No | Non-Lead - Plastic | No | 1979-01-24 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1979-01-24 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,42 | 8 Pleasant Street |  | No | No | Non-Lead - Copper | No | 1979-07-01 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1979-07-01 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,43 | 10 Pleasant Street |  | No | No | Non-Lead - Plastic | No | 1999-09-07 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1999-09-07 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,44 | 9 Pleasant Street |  | No | No | Non-Lead - Copper | No | 1999-09-07 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1999-09-07 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,45 | 17 Thurlows Hill |  | No | No | Non-Lead - Plastic | No | 2004-11-29 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2004-11-29 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-20 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | Yes
8B,46 | 15 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Copper | 2005-04-26 | 3/4 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-21 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,47 | 21 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 2003-04-15 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-08-21 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,49 | 25 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1999-02-08 | 3/4 | Installation date after lead ban | Yes | Mechanical excavation at one location | 2023-07-06 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,50 | 4 Pleasant Street |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1995-07-05 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,51 | 6 Pleasant Street |  | No | No | Non-Lead - Plastic | No | 1990-09-12 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1990-09-12 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,52 | 41 Thurlows Hill |  | No | No | Non-Lead - Copper | No | 2016 | 3/4 | Service line repair or replacement record | No |  |  |  | Non-Lead - Plastic | 1984-07-13 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-22 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,54 | 10 Granite Street |  | No | No | Non-Lead - Copper | No | 1987-08-25 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1987-10-26 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-25 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8B,55 | 10 Granite Street |  | No | No | Non-Lead - Copper | No | 1987-08-25 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 1987-10-26 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-09-25 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,56 | 14 Granite Street |  | No | No | Non-Lead - Copper | No | 1975-01-06 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2001-09-01 | 3/4 | Service line repair or replacement record | Yes | Visual inspection at the meter pit | 2024-09-27 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,59 | 22 Bayveiw Street |  | No | No | Non-Lead - Plastic | No | 2005-06-03 | 1 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 2005-06-03 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,60 | 15 Indian Point RD |  | No | No | Non-Lead - Copper | No | 1975-01-06 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1975-01-06 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,61 | 13 Indian Point RD |  | No | No | Non-Lead - Copper | No | 2002-09-09 | 3/4 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2002-09-09 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,64 | 28 Bayveiw Street |  | No | No | Non-Lead - Plastic | No | 2006-07-08 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2006-07-08 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,66 | 31 Indian Point RD |  | No | No | Non-Lead - Copper | No | 1975-01-15 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1975-01-15 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,68 | 35 Indian Point Rd |  | No | No | Non-Lead - Copper | No | 1976-07-28 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Copper | 1976-07-28 | 3/4 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-10-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,70 | 37 Indian Point RD |  | No | No | Non-Lead - Copper | No | 1975-01-17 | 3/4 | Installation record (e.g., tap card) | No |  |  |  | Non-Lead - Plastic | 1975-01-17 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-05-03 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,69 | 36 Bayveiw Streert |  | No | No | Non-Lead - Plastic | No | 2005-06-08 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2005-06-08 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-05-28 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,72A | 35 Bayveiw Street |  | No | No | Non-Lead - Plastic | No | 2005-06-08 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2005-06-08 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-10-02 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8B,73 | 31 Bayveiw Street |  | No | No | Non-Lead - Plastic | No | 2005-06-08 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2005-06-08 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-07-18 |  | Non-Lead | No | No |  | Building | No | Unknown | No
8B,75 | 25 Bayveiw Street |  | No | No | Non-Lead - Plastic | No | 2005-06-09 | 1 | Installation date after lead ban | No |  |  |  | Non-Lead - Plastic | 2005-06-09 | 1 | Installation date after lead ban | Yes | Visual inspection at the meter pit | 2024-06-21 |  | Non-Lead | No | No |  | Single Family Residence | No | Unknown | No
8A,14 | 36 Main Street |  | Yes - Multifamily Home | No | Non-Lead - Copper | No | 1975-08-15 | 3/4 | Installation record (e.g., tap card) | No |  |  | 5 unit apartment and resturant | Non-Lead - Plastic | 1975-08-15 | 1 | Installation record (e.g., tap card) | Yes | Visual inspection at the meter pit | 2024-08-21 |  | Non-Lead | No | No |  | Multiple Family Residence | No | Unknown | No

## Public Accessibility Doc.
Public Accessibility Documentation
PWS Name: Stonington Water Company
PWSID: ME0091510
Enter Date Last Updated: | October 8, 2024
Purpose of this worksheet: For systems to provide documentation to states on how they met the public accessibility requirements of the LCRR.
1. Select the location identifiers that you use for your service line inventory. Check all that apply.
Address
Street
Block
Intersection
Landmark
GPS Coordinates
Other
If "Other", please describe:
Tax map and lot information used as the Unique Service Line ID.
2. Does every service line have a location identifier? |  | Yes
If "No", explain. Remember that location identifiers are required for service lines that are lead and galvanized requiring replacement.
3. How are you making your inventory publicly accessible? Check all that apply. Remember that if your system serves > 50,000 people, you must provide the inventory online.
Interactive online map
Static online map
Online spreadsheet
Printed service line map
Printed tabular data
Information on water utility mailings or newsletter
Hard copy information available in water system office
Other
If "Other", please describe:
Customers will be notified on the Town's Facebook page and website, as well as in subsequent CCRs, that an electronic copy of the LSLI will be available for review on the Town website.

## State Checklist
State Checklist for Initial Inventory Submittal
PWS Name: Stonington Water Company
PWSID: ME0091510
Enter Date Last Updated:
Purpose of this worksheet: For states to determine and document if water systems met all of the January 15, 2021 Lead and Copper Rule (LCRR) requirements for their Initial Inventory including timely submission, required elements, use of information sources, public accessibility, and public notification of service line materials.
Part 1: Person Completing This Checklist
Name: | Title:
Telephone: | Email:
Part 2: Review for Timely Submission
1. Was the initial inventory submitted by the deadline of October 16, 2024? |  | Select "Yes" or "No"
Consider post-mark or date sent via email or reported into a state data system.
Part 3: Review for Required Elements
1. Does the inventory include all service lines connected to the distribution system? |  | Select "Yes" or "No"
Consider if the total number of service lines in the Inventory Summary worksheet, Part 3, matches sanitary survey and monitoring data in the state’s database (e.g., SDWIS/State) based on population served, number of service connections (including those for non-potable use), number of accounts, census data, or other information.
2. Does the inventory include portions owned by the water system and the customer? |  | Select "Yes" or "No"
Check the service line ownership type selected in the Inventory Summary worksheet, Part 1, Question 2a. If the system selected "Ownership is Split" check that their inventory includes information for both the system-owned and customer-owned portions.
3. Did the system classify all service lines as either Lead, Galvanized Requiring Replacement (GRR), Non-Lead, or Lead Status Unknown? |  | Select "Yes" or "No"
Consider if the system completed each row of the inventory summary table in the Inventory Summary worksheet, Part 3. Some rows may be zero.
4. In the space below, provide additional comments/documentation related to required elements of the system's initial inventory.
Part 4: Review for Information Sources
1. Did the system use the following historical records to prepare their initial inventory: previous materials evaluation, construction and plumbing codes/records, water system records, distribution system inspections and records. |  | Select "Yes" or "No"
Consider if the system identified historical records in each row of the Inventory Methods worksheet, Part 1, Rows 1 through 4. Consider if the system completed Row 5 if additional records are required in your state.
2. Is the system collecting service line material information during normal operations? |  | Select "Yes" or "No"
Consider if the system checked one or more normal operations activities in the Inventory Methods worksheet, Part 2. Consider asking the systems to submit updated or new standard operating procedures documenting service line material information collection.
3. Has the system conducted investigations to verify service line material? |  | Select "Yes" or "No"
This is not required by the LCRR but recommended by EPA to verify historical records and gather information where records do not exist to reduce the number of unknowns in the system as quickly as possible. Consider: • If the system checked one or more of the investigative methods on the Inventory Methods worksheet, Part 3. • If in their inventory, the system indicated that the materials classification was based on investigations. • The number of unknowns - EPA strongly discourages systems from submitting inventories with all unknowns. If all service line materials are lead status unknown, consider asking the water system to conduct investigations.
4. In the space below, provide additional comments related to information sources used to develop the system's initial inventory.
Part 5: Review for Public Accessibility
1. Does the inventory include location identifiers for each service line that is lead or galvanized requiring replacement? |  | Select "Yes" or "No"
Consider checking the inventory for location identifiers and reviewing the system's answers in the Public Accessibility Doc. worksheet, Questions 1 and 2.
2. Did the system make its inventory publicly accessible? |  | Select "Yes" or "No"
Consider reviewing the method by which the water system is making its inventory publicly accessible as identified in the Public Accessibility Doc. worksheet, Question 3. Check that systems serving more than 50,000 people have posted their service line inventories online.
3. In the space below, provide additional comments/documentation related to public accessibility of the system's initial inventory.
Part 6: Review of Customer Notification of Service Line Material
1. Does the water system's inventory consist of all Non-Lead Service lines? |  | Select "Yes" or "No"
If No, complete questions 2 through 5. If Yes, stop here.
2. Did the water system deliver the notification to people served by a lead service line (LSL), GRR, or lead status unknown service line within 30 days of completing the initial inventory? |  | Select "Yes" or "No"
3. Did the water system demonstrate that they delivered the notification and provide a copy of the notification to the state by July 1 for the previous calendar year? |  | Select "Yes" or "No"
4. Did the notification include the required content?
a. For confirmed LSLs, does the notification include: |  | Select "Yes" or "No" or "N/A"
· A statement that the service line material is lead,
· Information on lead health effects including mandatory health effects language of 40 CFR §141.85(a)(ii),
· Steps to minimize exposure to lead in drinking water,
· Opportunities for service line replacement,
· Available financing programs, and
· A statement that the system must replace its portion if the property owners notify the system that
they are replacing their portion?
b. For GRRs, does the notification include: |  | Select "Yes" or "No" or "N/A"
· A statement that the service line material is GRR,
· Information on lead health effects including mandatory health effects language of 40 CFR §141.85(a)(ii),
· Steps to minimize exposure to lead in drinking water, and
· Opportunities for service line replacement?
c. For Unknowns, does the notification include: |  | Select "Yes" or "No" or "N/A"
· A statement that the service line material is lead status unknown,
· Information on lead health effects including mandatory health effects language of 40 CFR §141.85(a)(ii),
· Steps to minimize exposure to lead in drinking water, and
· Opportunities to verify the service line material?
5. If the water system serves communities with a large proportion of non-English speaking consumers, as determined by the state, did they provide public education materials, including those in 40 CFR §141.85(e), in the appropriate language(s) or containing a telephone number or address where persons served may contact the water system to obtain a translated copy of the materials or to request assistance in the appropriate language? |  | Select "Yes" or "No"
6. In the space below, provide additional comments/documentation related to customer notification for people served by an LSL, GRR, or lead status unknown service line.

## Building Conditionals (hidden)
DRAFT | [8 empty] | Form Option For Customer Side | Classification | System-Owned Portion | Was Previously Lead? | Customer-Owned Portion | Classification for Entire Service Line | Single-Owned Portion | Classification for Entire Service Line
| Note to EPA: This is a background sheet to be hidden or deleted | [7 empty] | Lead | Lead | Lead |  | Lead | Lead | Lead | Lead
[9 empty] | Lead-lined galvanized | Lead | Lead |  | Galvanized | Lead | Galvanized | Non-Lead
[9 empty] | Galvanized | Galvanized | Lead |  | Non-Lead | Lead | Non-Lead | Non-Lead
[9 empty] | Non-Lead - Copper | Non-Lead | Lead |  | Material Unknown | Lead | Material Unknown | Lead Status Unknown
[9 empty] | Non-Lead - Plastic | Non-Lead | Galvanized |  | Lead | Lead
[9 empty] | Non-Lead - Other | Non-Lead | Galvanized |  | Galvanized | Non-Lead
[9 empty] | Unknown - Likely Lead | Material Unknown | Galvanized |  | Non-Lead | Non-Lead
[9 empty] | Unknown - Unlikely Lead | Material Unknown | Galvanized |  | Material Unknown | Lead Status Unknown
[9 empty] | Unknown - Material Unknown | Material Unknown | Non-Lead |  | Lead | Lead
[11 empty] | Non-Lead | Y | Galvanized | Galvanized Requiring Replacement
[9 empty] | Form Option For System Side | Classification | Non-Lead | N | Galvanized | Non-Lead
[9 empty] | Lead | Lead | Non-Lead | DN | Galvanized | Galvanized Requiring Replacement
[9 empty] | Lead-lined galvanized | Lead | Non-Lead |  | Non-Lead | Non-Lead
[9 empty] | Galvanized | Galvanized | Non-Lead |  | Material Unknown | Lead Status Unknown
[9 empty] | Non-Lead - Copper | Non-Lead | Material Unknown |  | Lead | Lead
[9 empty] | Non-Lead - Plastic | Non-Lead | Material Unknown |  | Galvanized | Galvanized Requiring Replacement
[9 empty] | Non-Lead - Other | Non-Lead | Material Unknown |  | Non-Lead | Lead Status Unknown
[9 empty] | Unknown - Likely Lead | Material Unknown | Material Unknown |  | Material Unknown | Lead Status Unknown
[9 empty] | Unknown - Unlikely Lead | Material Unknown
| system_owned_portion |  | customer_owned_portion | service_line_classification |  |  |  |  | Unknown - Material Unknown | Material Unknown
| System-Owned Portion | Was Previously Lead? | Customer-Owned Portion | Classification for Entire Service Line |  | IF( | ) AND ( | THEN
| Lead |  | Lead | Lead |  | IF(system_owned_portion=Lead) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | IF(system_owned_portion=Lead) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | IF(system_owned_portion="Lead") AND (customer_owned_portion="Lead" THEN service_line_classification="Lead"
| Lead |  | Galvanized | Lead | ELSE | IF(system_owned_portion=Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Lead | ELSEIF(system_owned_portion=Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Lead | ELSEIF(system_owned_portion="Lead") AND (customer_owned_portion="Galvanized Requiring Replacement" THEN service_line_classification="Lead"
| Lead |  | Non-Lead | Lead | ELSE | IF(system_owned_portion=Lead) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion=Lead) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion="Lead") AND (customer_owned_portion="Non-Lead" THEN service_line_classification="Lead"
| Lead |  | Material Unknown | Lead | ELSE | IF(system_owned_portion=Lead) AND (customer_owned_portion=Material Unknown THEN service_line_classification=Lead | ELSEIF(system_owned_portion=Lead) AND (customer_owned_portion=Material Unknown THEN service_line_classification=Lead | ELSEIF(system_owned_portion="Lead") AND (customer_owned_portion=Lead Status Unknown THEN service_line_classification="Lead"
| Galvanized |  | Lead | Lead | ELSE | IF(system_owned_portion=Galvanized) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion=Galvanized) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion="Galvanized1") AND (customer_owned_portion=Lead THEN service_line_classification="Lead"
| Galvanized |  | Galvanized | Non-Lead | ELSE | IF(system_owned_portion=Galvanized) AND (customer_owned_portion=Galvanized THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion=Galvanized) AND (customer_owned_portion=Galvanized THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion="Galvanized1") AND (customer_owned_portion="Galvanized2" THEN service_line_classification="Non-Lead"
| Galvanized |  | Non-Lead | Non-Lead | ELSE | IF(system_owned_portion=Galvanized) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion=Galvanized) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion="Galvanized1") AND (customer_owned_portion="Non-Lead" THEN service_line_classification="Non-Lead"
| Galvanized |  | Material Unknown | Lead Status Unknown | ELSE | IF(system_owned_portion=Galvanized) AND (customer_owned_portion=Material Unknown THEN service_line_classification=Lead Status Unknown | ELSEIF(system_owned_portion=Galvanized) AND (customer_owned_portion=Material Unknown THEN service_line_classification=Lead Status Unknown | ELSEIF(system_owned_portion="Galvanized1") AND (customer_owned_portion="Lead Status Unknown" THEN service_line_classification="Lead Status Unknown"
| Non-Lead |  | Lead | Lead | ELSE | IF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion="Non-Lead") AND (customer_owned_portion="Lead" THEN service_line_classification="Lead"
| Non-Lead |  | Galvanized | Galvanized Requiring Replacement | ELSE | IF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Galvanized Requiring Replacement | ELSEIF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Galvanized Requiring Replacement | ELSEIF(system_owned_portion="Non-Lead") AND (customer_owned_portion="Galvanized2" THEN service_line_classification="Non-Lead"
| Non-Lead |  | Galvanized | Non-Lead | ELSE | IF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion="Non-Lead") AND (customer_owned_portion="Non-Lead" THEN service_line_classification="Non-Lead"
| Non-Lead |  | Galvanized | Galvanized Requiring Replacement | ELSE | IF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Galvanized Requiring Replacement | ELSEIF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Galvanized THEN service_line_classification=Galvanized Requiring Replacement | ELSEIF(system_owned_portion="Non-Lead") AND (customer_owned_portion="Lead Status Unknown" THEN service_line_classification="Lead Status Unknown"
| Non-Lead |  | Non-Lead | Non-Lead | ELSE | IF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Non-Lead | ELSEIF(system_owned_portion="Non-Lead, but system is unable to demonstrate it was not previously Lead") AND (customer_owned_portion="Galvanized Requiring Replacement" THEN service_line_classification="Galvanized Requiring Replacement"
| Non-Lead |  | Material Unknown | Lead Status Unknown | ELSE | IF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Material Unknown THEN service_line_classification=Lead Status Unknown | ELSEIF(system_owned_portion=Non-Lead) AND (customer_owned_portion=Material Unknown THEN service_line_classification=Lead Status Unknown | ELSEIF(system_owned_portion="Lead Status Unknown") AND (customer_owned_portion="Lead" THEN service_line_classification="Lead"
| Material Unknown |  | Lead | Lead | ELSE | IF(system_owned_portion=Material Unknown) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion=Material Unknown) AND (customer_owned_portion=Lead THEN service_line_classification=Lead | ELSEIF(system_owned_portion="Lead Status Unknown") AND (customer_owned_portion="Galvanized Requiring Replacement" THEN service_line_classification="Galvanized Requiring Replacement"
| Material Unknown |  | Galvanized | Galvanized Requiring Replacement | ELSE | IF(system_owned_portion=Material Unknown) AND (customer_owned_portion=Galvanized THEN service_line_classification=Galvanized Requiring Replacement | ELSEIF(system_owned_portion=Material Unknown) AND (customer_owned_portion=Galvanized THEN service_line_classification=Galvanized Requiring Replacement | ELSEIF(system_owned_portion="Lead Status Unknown") AND (customer_owned_portion="Non-Lead" THEN service_line_classification="Lead Status Unknown"
| Material Unknown |  | Non-Lead | Lead Status Unknown | ELSE | IF(system_owned_portion=Material Unknown) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Lead Status Unknown | ELSEIF(system_owned_portion=Material Unknown) AND (customer_owned_portion=Non-Lead THEN service_line_classification=Lead Status Unknown | ELSEIF(system_owned_portion="Lead Status Unknown") AND (customer_owned_portion="Lead Status Unknown" THEN service_line_classification="Lead Status Unknown"
| Material Unknown |  | Material Unknown | Lead Status Unknown |  |  | ELSE service_line_classification = "CLASSIFICATION ERROR" | ELSE "CLASSIFICATION ERROR"

## Form Lists (hidden)
Tab | Form Control Lists
Detailed Inventory | Sensitive Population? (Y/N) | Service Line Material Classification* | If Non-Lead, Was Material Ever Previously Lead? | Basis of Material Classification | Was the Service Line Material Field Verified? | Select the Field Verification Method | Building Type Connected to Service Line | For CWSs, do Multi-family Residences (MFRs) Comprise at Least 20% of the Structures You Serve? | Is there a Lead Connector Present? | Point-of-Entry or Point-of-Use Treatment Present? | Does the Interior Building Plumbing Contain Copper Pipes with Lead Solder Installed before your State's Lead Ban (Generally 1986 - 1988) | Current LCR Sampling Site? | Building Type Connected to Service Line | For CWSs, do Multi-family Residences (MFRs) Comprise at Least 20% of the Structures You Serve? | Is there a Lead Connector Present? | Point-of-Entry or Point-of-Use Treatment Present? | Does the Interior Building Plumbing Contain Copper Pipes with Lead Solder Installed before your State's Lead Ban (Generally 1986 - 1988) | Current LCR Sampling Site?
| No | Lead | Yes | Previous materials evaluation | Yes | Visual inspection at meter pit | Single Family Residence | Yes | Yes | Yes | Yes | Yes | Single Family Residence | Yes | Yes | Yes | Yes | Yes
| Yes - School | Lead-lined galvanized | No | Installation record (e.g., tap card) | No | Customer self-identification | Multiple Family Residence | No | Known | No | No | No | Multiple Family Residence | No | Known | No | No | No
| Yes - Day Care | Galvanized | Don't know | Installation date is after the lead ban |  | CCTV Inspection at Curb Box - Internal | Building | N/A | Unknown | Unknown | Unknown |  | Building | N/A | Unknown | Unknown | Unknown
| Yes - Other | Non-Lead - Copper |  | Service line diameter is greater than 2 inches |  | CCTV inspection at Curb Box - External | Other | [5 empty] | Other
|  | Non-Lead - Plastic |  | Service line repair or replacement record |  | Water Quality Sampling - Targeted
|  | Non-Lead - Other |  | Statistical analysis |  | Water Quality Sampling - Flushed
|  | Unknown - Likely Lead |  | Field inspection only with no records |  | Water Quality Sampling - Sequential
|  | Unknown - Unlikely Lead |  | Water sampling only with no records |  | Water Quality Sampling - Other
|  | Unknown - Material Unknown |  | Other |  | Mechanical Excavation at 1 location
Mechanical Excavation at multiple locations
| Note to EPA: this is a background sheet to be hidden or deleted |  |  |  | Other